## Overview
Overview
This protocol applies to the communication between external systems and the Bluetti energy storage system. It enables real-time reading of the inverter's operational information and fault status, as well as control over the system's operation.
Physical Interface
Wi-Fi | Transmission Method |  | Max Frame Length |  | IP Address | Port | Checksum | Slave Address
| Modbus-TCP |  | 263Bytes |  | 192.168.8.1 | Webserver setting | None | 1~255 250:Summarize data
Protocol Specification |  | Data Type
|  | uint16 |  | int16 |  | uint32 |  | int32 | uint64 | string | enum | bool
|  | 16-bit unsigned integer |  | 16-bit signed integer |  | 32-bit unsigned integer |  | 32-bit signed integer | 64-bit unsigned integer | textual data | uint16 | 0 or 1
Note: Register Data principle: Little-end storage; Modbus Protocol transmission principle: Big-end transmission.
Function Code
|  | Function Code | Function |  |  |  | Address Type
|  | 0x03 | Read Multiple Holding Registers, Byte Operation |  |  |  | 4x
|  | 0x06 | Write Single Register, Byte Operation |  |  |  | 4x
|  | 0x10 | Write Multiple Registers, Byte Operation |  |  |  | 4x
Register Address Information
AC Meter
|  | Read | Read/Write
|  | 55101~55300 | /
Note:For detailed register address information, please refer to Table.

## Update Record
Cassandra Protocol
Version | Content | Date
Cassandra.V1.0 | first release | 2026.05.22

## Device list
Device Model | Modbus TCP Support | Webserver Configuration Support | Register Address Range | Firmware Version
SMeter | YES | YES | read:55101~55300
EBOX | YES | YES | /

## Meter
Cassandra register list
No. | register type | register address | register count | register abbreviation | data type | value range | remarks | unit | register property
1 | AC Meter | AC Meter Infomation
2 |  | 55111 | 1 | Status | uint16 | / | bit0/1:reserved bit2:Online status，0：offline；1：online。 | / | Read
3 |  | 55112 | 2 | Unix timestamp | uint32 | / |  | / | Read
4 |  | 55114 | 2 | Voltage A-N | float32 | / |  | V | Read
5 |  | 55116 | 2 | Voltage B-N | float32 | / |  | V | Read
6 |  | 55118 | 2 | Voltage C-N | float32 | / |  | V | Read
7 |  | 55120 | 2 | Current A | float32 | / |  | A | Read
8 |  | 55122 | 2 | Current B | float32 | / |  | A | Read
9 |  | 55124 | 2 | Current C | float32 | / |  | A | Read
10 |  | 55126 | 2 | Active power A | float32 | / |  | kW | Read
11 |  | 55128 | 2 | Active power B | float32 | / |  | kW | Read
12 |  | 55130 | 2 | Active power C | float32 | / |  | kW | Read
13 |  | 55132 | 2 | Reactive power A | float32 | / |  | kVAR | Read
14 |  | 55134 | 2 | Reactive power B | float32 | / |  | kVAR | Read
15 |  | 55136 | 2 | Reactive power C | float32 | / |  | kVAR | Read
16 |  | 55138 | 2 | Apparent power A | float32 | / |  | kVA | Read
17 |  | 55140 | 2 | Apparent power B | float32 | / |  | kVA | Read
18 |  | 55142 | 2 | Apparent power C | float32 | / |  | kVA | Read
19 |  | 55144 | 2 | Power factor A | float32 | / |  | / | Read
20 |  | 55146 | 2 | Power factor B | float32 | / |  | / | Read
21 |  | 55148 | 2 | Power factor C | float32 | / |  | / | Read
22 |  | 55150 | 2 | Average voltage L-N | float32 | / |  | V | Read
23 |  | 55152 | 2 | Average line current | float32 | / |  | A | Read
24 |  | 55154 | 2 | Unbalance line currents | float32 | / |  | % | Read
25 |  | 55156 | 2 | Total line currents | float32 | / |  | A | Read
26 |  | 55158 | 2 | Total active power | float32 | / |  | kW | Read
27 |  | 55160 | 2 | Total reactive power | float32 | / |  | kVAR | Read
28 |  | 55162 | 2 | Total apparent power | float32 | / |  | kVA | Read
29 |  | 55164 | 2 | Total power factor | float32 | / |  | / | Read
30 |  | 55166 | 2 | Frequency | float32 | / |  | Hz | Read
31 |  | 55168 | 2 | Total Import active energy | float32 | / |  | kWh | Read
32 |  | 55170 | 2 | Total Export active energy | float32 | / |  | kWh | Read