## Overview
Overview
This protocol applies to the communication between external systems and the Bluetti energy storage system. It enables real-time reading of the inverter's operational information and fault status, as well as control over the system's operation.
Physical Interface
Wi-Fi | Transmission Method |  | Max Frame Length |  | IP Address | Port | Checksum | Slave Address
| Modbus-TCP |  | 263Bytes |  | 192.168.8.1 | Webserver setting | None | 1~255 250:Summarize data
Protocol Specification |  | Data Type
|  | uint16 |  | int16 |  | uint32 |  | int32 | uint64 | string | enum | bool
|  | 16-bit unsigned integer |  | 16-bit signed integer |  | 32-bit unsigned integer |  | 32-bit signed integer | 64-bit unsigned integer | textual data | uint16 | 0 or 1
Note: Register Data principle: Little-end storage; Modbus Protocol transmission principle: Big-end transmission.
Function Code
|  | Function Code | Function |  |  |  | Address Type
|  | 0x03 | Read Multiple Holding Registers, Byte Operation |  |  |  | 4x
|  | 0x06 | Write Single Register, Byte Operation |  |  |  | 4x
|  | 0x10 | Write Multiple Registers, Byte Operation |  |  |  | 4x
Register Address Information
AC Meter
|  | Read | Read/Write
|  | 55101~55300 | /
Note:For detailed register address information, please refer to Table.

## Update Record
Cassandra Protocol
Version | Content | Date
Cassandra.V1.0 | first release | 2026.05.22
Cassandra.V1.1 | add BalcoXX registers | 2026.07.20
Cassandra.V1.2 | add EBOX registers page | 2026.08.07

## Device list
Device Model | Modbus TCP Support | Webserver Configuration Support | Register Address Range | Firmware Version
SMeter | YES | YES | read:55101~55300
EBOX | YES | YES | /
BalcoXX(inverter+battery) | YES | YES | read: Inverter Summary Information:50001~50027 Each Inverter Information:50200~50287 part; Inverter Set:57001~57017 Pack Summary Information:51001~51008 Each Pack Base Information:51200~51249 IOT:53001~53011 55101~55300 | IOT:500120117

## Meter
Cassandra register list
No. | register type | register address | register count | register abbreviation | data type | value range | remarks | unit | register property
1 | AC Meter | AC Meter Infomation
2 |  | 55111 | 1 | Status | uint16 | / | bit0/1:reserved bit2:Online status，0：offline；1：online。 | / | Read
3 |  | 55112 | 2 | Unix timestamp | uint32 | / |  | / | Read
4 |  | 55114 | 2 | Voltage A-N | float32 | / |  | V | Read
5 |  | 55116 | 2 | Voltage B-N | float32 | / |  | V | Read
6 |  | 55118 | 2 | Voltage C-N | float32 | / |  | V | Read
7 |  | 55120 | 2 | Current A | float32 | / |  | A | Read
8 |  | 55122 | 2 | Current B | float32 | / |  | A | Read
9 |  | 55124 | 2 | Current C | float32 | / |  | A | Read
10 |  | 55126 | 2 | Active power A | float32 | / |  | kW | Read
11 |  | 55128 | 2 | Active power B | float32 | / |  | kW | Read
12 |  | 55130 | 2 | Active power C | float32 | / |  | kW | Read
13 |  | 55132 | 2 | Reactive power A | float32 | / |  | kVAR | Read
14 |  | 55134 | 2 | Reactive power B | float32 | / |  | kVAR | Read
15 |  | 55136 | 2 | Reactive power C | float32 | / |  | kVAR | Read
16 |  | 55138 | 2 | Apparent power A | float32 | / |  | kVA | Read
17 |  | 55140 | 2 | Apparent power B | float32 | / |  | kVA | Read
18 |  | 55142 | 2 | Apparent power C | float32 | / |  | kVA | Read
19 |  | 55144 | 2 | Power factor A | float32 | / |  | / | Read
20 |  | 55146 | 2 | Power factor B | float32 | / |  | / | Read
21 |  | 55148 | 2 | Power factor C | float32 | / |  | / | Read
22 |  | 55150 | 2 | Average voltage L-N | float32 | / |  | V | Read
23 |  | 55152 | 2 | Average line current | float32 | / |  | A | Read
24 |  | 55154 | 2 | Unbalance line currents | float32 | / |  | % | Read
25 |  | 55156 | 2 | Total line currents | float32 | / |  | A | Read
26 |  | 55158 | 2 | Total active power | float32 | / |  | kW | Read
27 |  | 55160 | 2 | Total reactive power | float32 | / |  | kVAR | Read
28 |  | 55162 | 2 | Total apparent power | float32 | / |  | kVA | Read
29 |  | 55164 | 2 | Total power factor | float32 | / |  | / | Read
30 |  | 55166 | 2 | Frequency | float32 | / |  | Hz | Read
31 |  | 55168 | 2 | Total Import active energy | float32 | / |  | kWh | Read
32 |  | 55170 | 2 | Total Export active energy | float32 | / |  | kWh | Read

## BalcoXX
Cassandra register list
No. | register type | register address | register count | register abbreviation | data type | value range | remarks | unit | register property
| Inverter(AC/DC) | Inverter Summary Information
1 |  | 50001 | 1 | Number of Inverters | uint | 1~10 | One master,multiple slaves | / | Read
2 |  | 50002 | 2 | AC Load Power (Total) | uint | / | Total power output to AC loads | 1W | Read
3 |  | 50004 | 2 | PV Power (Total) | uint | / | Total PV power | 1W | Read
4 |  | 50006 | 2 | Grid Power (Total) | int | / | Total power of the grid | 1W | Read
5 |  | 50008 | 2 | Inverter Power (Total) | int | / | Total power of the inverter | 1W | Read
6 |  | 50010 | 2 | PV to AC Load Power | uint | / | direct_consumption Power | 1W | Read
7 |  | 50012 | 2 | AC Load Energy (Total) | uint | / | Total energy output to AC loads | 0.1kWh | Read
8 |  | 50014 | 2 | PV Charging Energy (Total) | uint | / | Total charging energy from PV to the system | 0.1kWh | Read
9 |  | 50016 | 2 | Grid Charging Energy (Total) | uint | / | Total charging energy from grid to the system | 0.1kWh | Read
10 |  | 50018 | 2 | Feed-in Grid Energy | uint | / | Feed into the grid | 0.1kWh | Read
11 |  | 50020 | 2 | PV to AC Load Energy | uint | / | / | 0.1kWh | Read
12 |  | 50022 | 1 | Inverter Operating Status | enum | 0~7 | 0:Stop 1:Off-Grid Operation 2:Grid-Connected Load 3:Grid-Connected Operation 4:Grid-Connected Charging 5:Grid-Connected Discharging 6:Inverter Fault 7:Abnormal Off-Grid | / | Read
13 |  | 50023 | 4 | Inverter Warning Information | uint | / | Different models correspond to different alarm information; please refer to the Inverter Fault Alarm Table. | / | Read
14 |  | 50027 | 5 | Inverter Fault Information | uint | / | Different models correspond to different fault information; please refer to the Inverter Fault Alarm Table. | / | Read
15 |  | Each Inverter Information
16 |  | 50200 | 6 | Inverter Type | string | / | Single inverter model 12 ASCII characters-normal string order | / | Read
17 |  | 50206 | 4 | Inverter SN Serial Number | uint | / | Serial number | / | Read
18 |  | 50210 | 2 | MCU1 Software Version | version | / | Main chip of the energy storage system | / | Read
19 |  | 50212 | 2 | MCU2 Software Version | version | / | Secondary chip of the energy storage system | / | Read
20 |  | 50214 | 1 | Grid Access Frequency | uint | / | / | 0.1Hz | Read
21 |  | 50215 | 2 | Grid Charging Power (Single) | int | / | Total grid charging power per inverter | 1W | Read
22 |  | 50217 | 2 | AC Load Power (Single) | uint | / | Total AC load power per inverter | 1W | Read
23 |  | 50219 | 2 | PV Charging Power (Single) | uint | / | Total PV charging power per inverter | 1W | Read
24 |  | 50221 | 2 | PV to AC Load Power (Single) | uint | / | PV to AC load power per inverter | 1W | Read
25 |  | 50223 | 2 | Grid Charging Energy (Single) | uint | / | Grid charging energy per inverter | 0.1kWh | Read
26 |  | 50225 | 2 | Feed-in Grid Energy (Single) | uint | / | Feed into the grid per inverter | 0.1kWh | Read
27 |  | 50227 | 2 | AC Load Energy (Single) | uint | / | Total energy output to AC loads per inverter | 0.1kWh | Read
28 |  | 50229 | 2 | PV Charging Energy (Single) | uint | / | Total charging energy from PV to the system per inverter | 0.1kWh | Read
29 |  | 50231 | 2 | PV to AC Load Energy (Single) | uint | / | PV to AC load energy per inverter | 0.1kWh | Read
30 |  | 50233 | 1 | Self Consumption Percent | uint | 0~100 | Calculation: 1 - (Grid-Supplied Energy / Total Load Energy Consumption) | 1% | Read
31 |  | 50234 | 1 | System Phase Number | uint | 0~3 | Grid connection phase number | / | Read
32 |  | 50235 | 1 | Grid1 Power | int/uint | / | The data type is determined by whether the device has a power feeding function; Devices without a power feeding function use uint,and vice versa for int. For the devices which have feed-in function:pruchasing electricity is positive,and feeding electricity is negative. | 1W | Read
33 |  | 50236 | 1 | Grid1 Voltage | uint | / | / | 0.1V | Read
34 |  | 50237 | 1 | Grid1 Current | int | / | / | 0.1A | Read
35 |  | 50238 | 1 | Grid2 Power | int/uint | / | The data type is determined by whether the device has a power feeding function; Devices without a power feeding function use uint,and vice versa for int. For the devices which have feed-in function:pruchasing electricity is positive,and feeding electricity is negative. | 1W | Read
36 |  | 50239 | 1 | Grid2 Voltage | uint | / | / | 0.1V | Read
37 |  | 50240 | 1 | Grid2 Current | int | / | / | 0.1A | Read
38 |  | 50241 | 1 | Grid3 Power | int/uint | / | The data type is determined by whether the device has a power feeding function; Devices without a power feeding function use uint,and vice versa for int. For the devices which have feed-in function:pruchasing electricity is positive,and feeding electricity is negative. | 1W | Read
39 |  | 50242 | 1 | Grid3 Voltage | uint | / | / | 0.1V | Read
40 |  | 50243 | 1 | Grid3 Current | int | / | / | 0.1A | Read
41 |  | 50244 | 1 | AC System Phase Number | uint | [1, 2, 3] | Number of AC load output phases | / | Read
42 |  | 50245 | 1 | AC Load1 Power | uint | / | / | 1W | Read
43 |  | 50246 | 1 | AC Load1 Voltage | uint | / | / | 0.1V | Read
44 |  | 50247 | 1 | AC Load1 Current | uint | / | / | 0.1A | Read
45 |  | 50248 | 1 | AC Load2 Power | uint | / | / | 1W | Read
46 |  | 50249 | 1 | AC Load2 Voltage | uint | / | / | 0.1V | Read
47 |  | 50250 | 1 | AC Load2 Current | uint | / | / | 0.1A | Read
48 |  | 50251 | 1 | AC Load3 Power | uint | / | / | 1W | Read
49 |  | 50252 | 1 | AC Load3 Voltage | uint | / | / | 0.1V | Read
50 |  | 50253 | 1 | AC Load3 Current | uint | / | / | 0.1A | Read
51 |  | 50254 | 1 | Inverter System Phase Number | uint | [1, 2, 3] | Number of Inverter phases | / | Read
52 |  | 50255 | 1 | Inverter1 Operation Status | enum | [0,1,2,3,4,5] | 0:Stop 1:Off-Grid Operation 2:Grid-Connected Load 3:Grid-Connected Operation 4:Grid-Connected Charging 5:Grid-Connected Discharging | / | Read
53 |  | 50256 | 1 | Inverter1 Power | uint | / | / | 1W | Read
54 |  | 50257 | 1 | Inverter1 Voltage | uint | / | / | 0.1V | Read
55 |  | 50258 | 1 | Inverter1 Current | uint | / | / | 0.1A | Read
56 |  | 50259 | 1 | Inverter2 Operation Status | enum | [0,1,2,3,4,5] | 0:Stop 1:Off-Grid Operation 2:Grid-Connected Load 3:Grid-Connected Operation 4:Grid-Connected Charging 5:Grid-Connected Discharging | / | Read
57 |  | 50260 | 1 | Inverter2 Power | uint | / | / | 1W | Read
58 |  | 50261 | 1 | Inverter2 Voltage | uint | / | / | 0.1V | Read
59 |  | 50262 | 1 | Inverter2 Current | uint | / | / | 0.1A | Read
60 |  | 50263 | 1 | Inverter3 Operation Status | enum | [0,1,2,3,4,5] | 0:Stop 1:Off-Grid Operation 2:Grid-Connected Load 3:Grid-Connected Operation 4:Grid-Connected Charging 5:Grid-Connected Discharging | / | Read
61 |  | 50264 | 1 | Inverter3 Power | uint | / | / | 1W | Read
62 |  | 50265 | 1 | Inverter3 Voltage | uint | / | / | 0.1V | Read
63 |  | 50266 | 1 | Inverter3 Current | uint | / | / | 0.1A | Read
64 |  | 50267 | 1 | PV Total Number | enum | [0,1,2,3,4] | PV connection quantity per inverter bit0~bit3:Number of DC PV bit4~bit7:Number of AC PV | / | Read
65 |  | 50268 | 1 | PV1 Type | enum | [0,1,2,3] | General: 0:reserve 1:CAR 2:Adapter 3:other Only available on some models: 100:DC PV 101:AC PV | / | Read
66 |  | 50269 | 1 | PV1 Input Power | uint | / | PV1 charging power | 1W | Read
67 |  | 50270 | 1 | PV1 Input Voltage | uint | / | PV1 charging voltage | 0.1V | Read
68 |  | 50271 | 1 | PV1 Input Current | uint | / | PV1 charging current | 0.1A | Read
69 |  | 50272 | 1 | PV2 Type | enum | [0,1,2,3] | General: 0:reserve 1:CAR 2:Adapter 3:other Only available on some models: 100:DC PV 101:AC PV | / | Read
70 |  | 50273 | 1 | PV2 Input Power | uint | / | PV2 charging power | 2W | Read
71 |  | 50274 | 1 | PV2 Input Voltage | uint | / | PV2 charging voltage | 0.2V | Read
72 |  | 50275 | 1 | PV2 Input Current | uint | / | PV2 charging current | 0.2A | Read
73 |  | 50276 | 1 | PV3 Type | enum | [0,1,2,3] | General: 0:reserve 1:CAR 2:Adapter 3:other Only available on some models: 100:DC PV 101:AC PV | / | Read
74 |  | 50277 | 1 | PV3 Input Power | uint | / | PV3 charging power | 3W | Read
75 |  | 50278 | 1 | PV3 Input Voltage | uint | / | PV3 charging voltage | 0.3V | Read
76 |  | 50279 | 1 | PV3 Input Current | uint | / | PV3 charging current | 0.3A | Read
77 |  | 50280 | 1 | PV4 Type | enum | [0,1,2,3] | General: 0:reserve 1:CAR 2:Adapter 3:other Only available on some models: 100:DC PV 101:AC PV | / | Read
78 |  | 50281 | 1 | PV4 Input Power | uint | / | PV4 charging power | 4W | Read
79 |  | 50282 | 1 | PV4 Input Voltage | uint | / | PV4 charging voltage | 0.4V | Read
80 |  | 50283 | 1 | PV4 Input Current | uint | / | PV4 charging current | 0.4A | Read
81 |  | 50284 | 1 | PV5 Type | enum | [0,1,2,3] | General: 0:reserve 1:CAR 2:Adapter 3:other Only available on some models: 100:DC PV 101:AC PV | / | Read
82 |  | 50285 | 1 | PV5 Input Power | uint | / | PV5 charging power | 5W | Read
83 |  | 50286 | 1 | PV5 Input Voltage | uint | / | PV5 charging voltage | 0.5V | Read
84 |  | 50287 | 1 | PV5 Input Current | uint | / | PV5 charging current | 0.5A | Read
85 |  | 57001 | 1 | AC load output switch | bool | [0,1] | 0：Off；1: On | / | Read/Write
86 |  | 57009 | 1 | AC grid charging switch | bool | [0,1] | 0：Off；1: On | / | Read/Write
87 |  | 57010 | 1 | AC grid feed-in switch | bool | [0,1] | 0：Off；1: On | / | Read/Write
88 |  | 57016 | 1 | Battery empty SOC threshold | uint | 0~100 | Stop discharge when it reaches this value. | % | Read/Write
89 |  | 57017 | 1 | Battery full SOC threshold | uint | 0~100 | Stop charge when it reaches this value. | % | Read/Write
90 | Battery | Pack Summary Information
91 |  | 51001 | 1 | Total Pack Parallel Quantity | uint | 1~16 | Quantity of parallel-connected Packs | / | Read
92 |  | 51002 | 1 | Total Pack Voltage | uint | 0~10000 | / | 0.1V | Read
93 |  | 51003 | 1 | Total Pack Current | uint | / | / | 0.1A | Read
94 |  | 51004 | 1 | Total Pack SOC | uint | 0~100 | Total state of charge | % | Read
95 |  | 51005 | 1 | Total Pack SOH | uint | 0~100 | Total state of health | % | Read
96 |  | 51006 | 1 | Total Pack Charging Status | enum | [0,1,2] | 0:Idle 1:Charging 2:Discharging | / | Read
97 |  | 51007 | 1 | Total Estimated Full Charge Time | uint | / | / | 1Min | Read
98 |  | 51008 | 1 | Total Estimated Full Discharge Time | uint | / | / | 1Min | Read
99 |  | Each Pack Base Information
100 |  | 51200 | 6 | Pack Type | string | 1~12 | Pack type 12 ASCII characters-normal string order | / | Read
101 |  | 51206 | 4 | Pack SN Serial Number | uint | / | Serial Number | / | Read
102 |  | 51210 | 1 | Total Pack Software Number | uint | 1~10 | For the same version,only the lowest one is displayed | / | Read
103 |  | 51211 | 2 | Pack Software Version1 | uint | / | / | / | Read
104 |  | 51213 | 2 | Pack Software Version2 | uint | / | / | / | Read
105 |  | 51215 | 2 | Pack Software Version3 | uint | / | / | / | Read
106 |  | 51217 | 2 | Pack Software Version4 | uint | / | / | / | Read
107 |  | 51219 | 1 | Pack Voltage | uint | 0~10000 | / | 0.1V | Read
108 |  | 51220 | 1 | Pack Current | uint | 0~10000 | During charging,it refers to the charging current; During discharging,it refers to the discharging current. | 0.1A | Read
109 |  | 51221 | 1 | Pack SOC | uint | 0~100 | Single pack state of charge | % | Read
110 |  | 51222 | 1 | Pack SOH | uint | 0~100 | Single pack state of health | % | Read
111 |  | 51223 | 1 | Pack Cycle Count | uint | / | A complete charge-discharge process constitutes one cycle | / | Read
112 |  | 51224 | 1 | Pack Average Temperature | int | [-40~160] | / | 1℃ | Read
113 |  | 51234 | 1 | Pack Total Cell Count | uint | / | / | / | Read
114 |  | 51235 | 1 | Pack Total NTC Count | uint | 1~255 | / | / | Read
115 |  | 51236 | 2 | Pack Total Charging Energy | uint | / | Cumulative charging energy of the pack | 1Wh | Read
116 |  | 51238 | 2 | Pack Total Discharging Energy | uint | / | Cumulative discharging energy of the pack | 1Wh | Read
117 |  | 51240 | 2 | Pack Protect | uint | / | The BMS will disable input/output; bitwise representation | / | Read
118 |  | 51242 | 3 | Pack System Error | uint | / | The BMS will disable input/output; bitwise representation | / | Read
119 |  | 51245 | 1 | Pack Alarm (Residential ESS) | uint | / | Notify the upper system cease charging or discharging For detailed information, please refer to the Pack Alarm Table Sheet1 | / | Read
120 |  | 51246 | 2 | Pack Alarm (Portable ESS) | uint | / | For detailed information, please refer to the Pack Alarm Table Sheet2 | / | Read
121 |  | 51248 | 1 | Pack Estimated Full Charge Time | uint | / | / | 1Min | Read
122 |  | 51249 | 1 | Pack Estimated Full Discharge Time | uint | / | / | 1Min | Read
123 | IOT/HMI/common | IOT Basic Information/Monitoring Module Basic Information
124 |  | 53001 | 6 | IoT Model | string | / | Indicate the inverter main pack type | / | Read
125 |  | 53007 | 4 | IoT SN | uint | / | Serial number | / | Read
126 |  | 53011 | 2 | IoT Software Version | version | / | / | / | Read

## EBOX
Cassandra register list
No. | register type | register address | register count | register abbreviation | data type | value range | remarks | unit | register property
| Inverter(AC/DC) | Inverter Summary Information
1 |  | 50001 | 1 | Number of Inverters | uint | 1~10 | One master,multiple slaves | / | Read
2 |  | 50002 | 2 | AC Load Power (Total) | uint | / | Total power output to AC loads | 1W | Read
3 |  | 50004 | 2 | PV Power (Total) | uint | / | Total PV power | 1W | Read
4 |  | 50006 | 2 | Grid Power (Total) | int | / | Total power of the grid | 1W | Read
5 |  | 50008 | 2 | Inverter Power (Total) | int | / | Total power of the inverter | 1W | Read
6 |  | 50010 | 2 | PV to AC Load Power | uint | / | direct_consumption Power | 1W | Read
7 |  | 50012 | 2 | AC Load Energy (Total) | uint | / | Total energy output to AC loads | 0.1kWh | Read
8 |  | 50014 | 2 | PV Charging Energy (Total) | uint | / | Total charging energy from PV to the system | 0.1kWh | Read
9 |  | 50016 | 2 | Grid Charging Energy (Total) | uint | / | Total charging energy from grid to the system | 0.1kWh | Read
10 |  | 50018 | 2 | Feed-in Grid Energy | uint | / | Feed into the grid | 0.1kWh | Read
11 |  | 50020 | 2 | PV to AC Load Energy | uint | / | / | 0.1kWh | Read
12 |  | 50022 | 1 | Inverter Operating Status | enum | 0~7 | 0:Stop 1:Off-Grid Operation 2:Grid-Connected Load 3:Grid-Connected Operation 4:Grid-Connected Charging 5:Grid-Connected Discharging 6:Inverter Fault 7:Abnormal Off-Grid | / | Read
13 |  | 50023 | 4 | Inverter Warning Information | uint | / | Different models correspond to different alarm information; please refer to the Inverter Fault Alarm Table. | / | Read
14 |  | 50027 | 5 | Inverter Fault Information | uint | / | Different models correspond to different fault information; please refer to the Inverter Fault Alarm Table. | / | Read
|  | 50032 | 16 | Manufacturer information | ASCII |  |  |  | Read
|  | 50048 | 2 | inverter_grid_port_Reactive power_Sum | int32 |  |  | 1Var | Read
|  | 50050 | 2 | inverter_grid_port_apparent power_Sum | int32 |  |  | 1VA | Read
|  | 50052 | 2 | Battery power | int32 |  |  | 1W | Read
|  | 50054 | 2 | Rated maximum active power capacity of the inverter/pMax | int32 |  |  |  | Read
|  | 50056 | 2 | Maximum continuous active power output capability of the DER | int32 |  | rtgMaxW |  | Read
|  | 50058 | 2 | Maximum continuous apparent power output capability of the DER | int32 |  | rtgMaxVA |  | Read
|  | 50060 | 2 | Maximum continuous reactive power received by the DER | int32 |  | rtgMaxVar |  | Read
|  | 50062 | 2 | Maximum continuous reactive power received by the DER | int32 |  | rtgMaxVarNeg |  | Read
|  | 50064 | 2 | Minimum power factor when injecting reactive power | int32 |  | rtgMinPFOverExcited |  | Read
|  | 50066 | 2 | Minimum power factor when absorbing reactive power | int32 |  | rtgMinPFUnderExcited |  | Read
|  | 50068 | 1 | Online_Component | / |  | Accessory Online Status: 0: offline; 1: online bit0: reserved bit1: reserved bit2: Grid Meter Online Status (Added in Protocol 2011) bit3: Load Meter Online Status bit4~15:reserved |  | Read
|  | 50069 |  | Rated_Voltage | int32 | 0-65535 |  | 1V | Read
|  | 50070 |  | Rated_Frequency | int32 | 0-65535 |  | 0.01HZ | Read
15 |  | Each Inverter Information
16 |  | 50200 | 6 | Inverter Type | string | / | Single inverter model 12 ASCII characters-normal string order | / | Read
17 |  | 50206 | 4 | Inverter SN Serial Number | uint | / | Serial number | / | Read
18 |  | 50210 | 2 | MCU1 Software Version | version | / | Main chip of the energy storage system | / | Read
19 |  | 50212 | 2 | MCU2 Software Version | version | / | Secondary chip of the energy storage system | / | Read
20 |  | 50214 | 1 | Grid Access Frequency | uint | / | / | 0.1Hz | Read
21 |  | 50215 | 2 | Grid Charging Power (Single) | int | / | Total grid charging power per inverter | 1W | Read
22 |  | 50217 | 2 | AC Load Power (Single) | uint | / | Total AC load power per inverter | 1W | Read
23 |  | 50219 | 2 | PV Charging Power (Single) | uint | / | Total PV charging power per inverter | 1W | Read
24 |  | 50221 | 2 | PV to AC Load Power (Single) | uint | / | PV to AC load power per inverter | 1W | Read
25 |  | 50223 | 2 | Grid Charging Energy (Single) | uint | / | Grid charging energy per inverter | 0.1kWh | Read
26 |  | 50225 | 2 | Feed-in Grid Energy (Single) | uint | / | Feed into the grid per inverter | 0.1kWh | Read
27 |  | 50227 | 2 | AC Load Energy (Single) | uint | / | Total energy output to AC loads per inverter | 0.1kWh | Read
28 |  | 50229 | 2 | PV Charging Energy (Single) | uint | / | Total charging energy from PV to the system per inverter | 0.1kWh | Read
29 |  | 50231 | 2 | PV to AC Load Energy (Single) | uint | / | PV to AC load energy per inverter | 0.1kWh | Read
30 |  | 50233 | 1 | Self Consumption Percent | uint | 0~100 | Calculation: 1 - (Grid-Supplied Energy / Total Load Energy Consumption) | 1% | Read
31 |  | 50234 | 1 | System Phase Number | uint | 0~3 | Grid connection phase number | / | Read
32 |  | 50235 | 1 | Grid1 Power | int/uint | / | The data type is determined by whether the device has a power feeding function; Devices without a power feeding function use uint,and vice versa for int. For the devices which have feed-in function:pruchasing electricity is positive,and feeding electricity is negative. | 1W | Read
33 |  | 50236 | 1 | Grid1 Voltage | uint | / | / | 0.1V | Read
34 |  | 50237 | 1 | Grid1 Current | int | / | / | 0.1A | Read
35 |  | 50238 | 1 | Grid2 Power | int/uint | / | The data type is determined by whether the device has a power feeding function; Devices without a power feeding function use uint,and vice versa for int. For the devices which have feed-in function:pruchasing electricity is positive,and feeding electricity is negative. | 1W | Read
36 |  | 50239 | 1 | Grid2 Voltage | uint | / | / | 0.1V | Read
37 |  | 50240 | 1 | Grid2 Current | int | / | / | 0.1A | Read
38 |  | 50241 | 1 | Grid3 Power | int/uint | / | The data type is determined by whether the device has a power feeding function; Devices without a power feeding function use uint,and vice versa for int. For the devices which have feed-in function:pruchasing electricity is positive,and feeding electricity is negative. | 1W | Read
39 |  | 50242 | 1 | Grid3 Voltage | uint | / | / | 0.1V | Read
40 |  | 50243 | 1 | Grid3 Current | int | / | / | 0.1A | Read
41 |  | 50244 | 1 | AC System Phase Number | uint | [1, 2, 3] | Number of AC load output phases | / | Read
42 |  | 50245 | 1 | AC Load1 Power | uint | / | / | 1W | Read
43 |  | 50246 | 1 | AC Load1 Voltage | uint | / | / | 0.1V | Read
44 |  | 50247 | 1 | AC Load1 Current | uint | / | / | 0.1A | Read
45 |  | 50248 | 1 | AC Load2 Power | uint | / | / | 1W | Read
46 |  | 50249 | 1 | AC Load2 Voltage | uint | / | / | 0.1V | Read
47 |  | 50250 | 1 | AC Load2 Current | uint | / | / | 0.1A | Read
48 |  | 50251 | 1 | AC Load3 Power | uint | / | / | 1W | Read
49 |  | 50252 | 1 | AC Load3 Voltage | uint | / | / | 0.1V | Read
50 |  | 50253 | 1 | AC Load3 Current | uint | / | / | 0.1A | Read
51 |  | 50254 | 1 | Inverter System Phase Number | uint | [1, 2, 3] | Number of Inverter phases | / | Read
52 |  | 50255 | 1 | Inverter1 Operation Status | enum | [0,1,2,3,4,5] | 0:Stop 1:Off-Grid Operation 2:Grid-Connected Load 3:Grid-Connected Operation 4:Grid-Connected Charging 5:Grid-Connected Discharging | / | Read
53 |  | 50256 | 1 | Inverter1 Power | uint | / | / | 1W | Read
54 |  | 50257 | 1 | Inverter1 Voltage | uint | / | / | 0.1V | Read
55 |  | 50258 | 1 | Inverter1 Current | uint | / | / | 0.1A | Read
56 |  | 50259 | 1 | Inverter2 Operation Status | enum | [0,1,2,3,4,5] | 0:Stop 1:Off-Grid Operation 2:Grid-Connected Load 3:Grid-Connected Operation 4:Grid-Connected Charging 5:Grid-Connected Discharging | / | Read
57 |  | 50260 | 1 | Inverter2 Power | uint | / | / | 1W | Read
58 |  | 50261 | 1 | Inverter2 Voltage | uint | / | / | 0.1V | Read
59 |  | 50262 | 1 | Inverter2 Current | uint | / | / | 0.1A | Read
60 |  | 50263 | 1 | Inverter3 Operation Status | enum | [0,1,2,3,4,5] | 0:Stop 1:Off-Grid Operation 2:Grid-Connected Load 3:Grid-Connected Operation 4:Grid-Connected Charging 5:Grid-Connected Discharging | / | Read
61 |  | 50264 | 1 | Inverter3 Power | uint | / | / | 1W | Read
62 |  | 50265 | 1 | Inverter3 Voltage | uint | / | / | 0.1V | Read
63 |  | 50266 | 1 | Inverter3 Current | uint | / | / | 0.1A | Read
64 |  | 50267 | 1 | PV Total Number | enum | [0,1,2,3,4] | PV connection quantity per inverter bit0~bit3:Number of DC PV bit4~bit7:Number of AC PV | / | Read
65 |  | 50268 | 1 | PV1 Type | enum | [0,1,2,3] | General: 0:reserve 1:CAR 2:Adapter 3:other Only available on some models: 100:DC PV 101:AC PV | / | Read
66 |  | 50269 | 1 | PV1 Input Power | uint | / | PV1 charging power | 1W | Read
67 |  | 50270 | 1 | PV1 Input Voltage | uint | / | PV1 charging voltage | 0.1V | Read
68 |  | 50271 | 1 | PV1 Input Current | uint | / | PV1 charging current | 0.1A | Read
69 |  | 50272 | 1 | PV2 Type | enum | [0,1,2,3] | General: 0:reserve 1:CAR 2:Adapter 3:other Only available on some models: 100:DC PV 101:AC PV | / | Read
70 |  | 50273 | 1 | PV2 Input Power | uint | / | PV2 charging power | 2W | Read
71 |  | 50274 | 1 | PV2 Input Voltage | uint | / | PV2 charging voltage | 0.2V | Read
72 |  | 50275 | 1 | PV2 Input Current | uint | / | PV2 charging current | 0.2A | Read
73 |  | 50276 | 1 | PV3 Type | enum | [0,1,2,3] | General: 0:reserve 1:CAR 2:Adapter 3:other Only available on some models: 100:DC PV 101:AC PV | / | Read
74 |  | 50277 | 1 | PV3 Input Power | uint | / | PV3 charging power | 3W | Read
75 |  | 50278 | 1 | PV3 Input Voltage | uint | / | PV3 charging voltage | 0.3V | Read
76 |  | 50279 | 1 | PV3 Input Current | uint | / | PV3 charging current | 0.3A | Read
77 |  | 50280 | 1 | PV4 Type | enum | [0,1,2,3] | General: 0:reserve 1:CAR 2:Adapter 3:other Only available on some models: 100:DC PV 101:AC PV | / | Read
78 |  | 50281 | 1 | PV4 Input Power | uint | / | PV4 charging power | 4W | Read
79 |  | 50282 | 1 | PV4 Input Voltage | uint | / | PV4 charging voltage | 0.4V | Read
80 |  | 50283 | 1 | PV4 Input Current | uint | / | PV4 charging current | 0.4A | Read
81 |  | 50284 | 1 | PV5 Type | enum | [0,1,2,3] | General: 0:reserve 1:CAR 2:Adapter 3:other Only available on some models: 100:DC PV 101:AC PV | / | Read
82 |  | 50285 | 1 | PV5 Input Power | uint | / | PV5 charging power | 5W | Read
83 |  | 50286 | 1 | PV5 Input Voltage | uint | / | PV5 charging voltage | 0.5V | Read
84 |  | 50287 | 1 | PV5 Input Current | uint | / | PV5 charging current | 0.5A | Read
|  | 50288 | 2 | inverter_grid_port_Active power_phase A | int32 |  |  |  | Read
|  | 50290 | 2 | inverter_grid_port_Active power_phase B | int32 |  |  |  | Read
|  | 50292 | 2 | inverter_grid_port_Active power_phase C | int32 |  |  |  | Read
|  | 50294 | 2 | inverter_grid_port_Reactive power_phase A | int32 |  |  |  | Read
|  | 50296 | 2 | inverter_grid_port_Reactive power_phase B | int32 |  |  |  | Read
|  | 50298 | 2 | inverter_grid_port_Reactive power_phase C | int32 |  |  |  | Read
|  | 50300 | 2 | inverter_grid_port_apparent power_phase A | int32 |  |  |  | Read
|  | 50302 | 2 | inverter_grid_port_apparent power_phase B | int32 |  |  |  | Read
|  | 50304 | 2 | inverter_grid_port_apparent power_phase C | int32 |  |  |  | Read
|  | 50306 | 2 | inverter_internal_port_Active power_phase A | int32 |  |  |  | Read
|  | 50308 | 2 | inverter_internal_port_Active power_phase B | int32 |  |  |  | Read
|  | 50310 | 2 | inverter_internal_port_Active power_phase C | int32 |  |  |  | Read
|  | 50400 | 2 | hw_version | ASCII |  | HwVer:5.0 ASCII |  | Read
|  | 50402 | 1 | active_power | int16 |  | 1 watts,INT16 | 1w | Read
|  | 50403 | 1 | reactive_power | int16 |  | 1 vars,INT16 | 1Var | Read
|  | 50404 | 1 | freq | uint16 |  | 0.01 hertz |  | Read
|  | 50405 | 1 | operationalModeState | enum |  | 0 = Not applicable/Unknown 1 = Off 2 = Operational mode 3 = Test mode |  | Read
|  | 50406 | 1 | connection_status | enum |  | 0 = Connected 1 = Available 2 = Operating 3 = Test 4 = Fault/Error |  | Read
|  | 50407 | 1 | alarmStatus | enum |  | BitMap 0 = DER_FAULT_OVER_CURRENT 1 = DER_FAULT_OVER_VOLTAGE 2 = DER_FAULT_UNDER_VOLTAGE 3 = DER_FAULT_OVER_FREQUENCY 4 = DER_FAULT_UNDER_FREQUENCY 5 = DER_FAULT_VOLTAGE_IMBALANCE 6 = DER_FAULT_CURRENT_IMBALANCE 7 = DER_FAULT_EMERGENCY_LOCAL 8 = DER_FAULT_EMERGENCY_REMOTE 9 = DER_FAULT_LOW_POWER_INPUT 10 = DER_FAULT_PHASE_ROTATION |  | Read
|  | 50408 | 1 | inverterStatus | enum |  | 0 - N/A 1 - off 2 - sleeping (auto-shutdown) or DER is at low output power/voltage 3 - starting up or ON but not producing power 4 - tracking MPPT power point 5 - forced power reduction/derating 6 - shutting down 7 - one or more faults exist 8 - standby (service on unit) - DER may be at high output voltage/power 9 - test mode 10 - as defined in manufacturer status All other values reserved. |  | Read
|  | 50409 | 1 | localControlModeStatus | enum |  | 0 – local control 1 – remote control All other values reserved. |  | Read
|  | 50410 | 1 | storageModeStatus | enum |  | 0 – storage charging 1 – storage discharging 2 – storage holding All other values reserved. |  | Read
85 |  | 57001 | 1 | AC load output switch | bool | [0,1] | 0：Off；1: On | / | Read/Write
86 |  | 57009 | 1 | AC grid charging switch | bool | [0,1] | 0：Off；1: On | / | Read/Write
87 |  | 57010 | 1 | AC grid feed-in switch | bool | [0,1] | 0：Off；1: On | / | Read/Write
88 |  | 57016 | 1 | Battery empty SOC threshold | uint | 0~100 | Stop discharge when it reaches this value. | % | Read/Write
89 |  | 57017 | 1 | Battery full SOC threshold | uint | 0~100 | Stop charge when it reaches this value. | % | Read/Write
|  | 57030 | 1 | EMS_CTRL | enum | [4,6] | bit0~3: remote control enable: 6-remote control enable; 4_remote control disable(DER self control) bit4~15: reserved | / | Write/Read
|  | 57031 | 1 | reserved
|  | 57032 | 2 | P_inv_active_target_L1 | int32 |  | feedback to grid is positive; charge in is negative; 0xFFFFFFFF= invalid; | 1w | Write/Read
|  | 57034 | 2 | P_inv_active_target_L2 | int32 |  | feedback to grid is positive; charge in is negative; 0xFFFFFFFF= invalid; | 1w | Write/Read | dark: reserved
|  | 57036 | 2 | P_inv_active_target_L3 | int32 |  | feedback to grid is positive; charge in is negative; 0xFFFFFFFF= invalid; | 1w | Write/Read
|  | 57038 | 2 | P_inv_reactive_target_L1 | int32 |  | feedback to grid is positive; charge in is negative; 0xFFFFFFFF= invalid; | Var | Write/Read
|  | 57040 | 2 | P_inv_reactive_target_L2 | int32 |  | feedback to grid is positive; charge in is negative; 0xFFFFFFFF= invalid; | Var | Write/Read
|  | 57042 | 2 | P_inv_reactive_target_L3 | int32 |  | feedback to grid is positive; charge in is negative; 0xFFFFFFFF= invalid; | Var | Write/Read
|  | 57044 | 2 | P_inv_apparent_target_L1 | int32 |  | feedback to grid is positive; charge in is negative; 0xFFFFFFFF= invalid; | VA | Write/Read
|  | 57046 | 2 | P_inv_apparent_target_L2 | int32 |  | feedback to grid is positive; charge in is negative; 0xFFFFFFFF= invalid; | VA | Write/Read
|  | 57048 | 2 | P_inv_apparent_target_L3 | int32 |  | feedback to grid is positive; charge in is negative; 0xFFFFFFFF= invalid; | VA | Write/Read
|  | 57050 | 1 | Active power output level specified as % of maximum rated active power output | int16 | -100~100 | feedback to grid is positive; charge in is negative; | %Wmax | Write/Read
|  | 57051 | 1 | Timeout period for power limit. |  |  | WLimPctRvrtTms;default 600s | Secs | Write/Read
|  | 57052 | 1 | Ramp time for moving from current setpoint to new setpoint. |  | 暂不支持 | WLimPctRmpTms | Secs | Write/Read
|  | 57053 | 1 | Ramp rate expressed as %(WMax)/s for moving from current setpoint to new setpoint. |  | 暂不支持 | WLimPctRmpPct | %Wmax/s | Write/Read
|  | 57503 | 1 | battery Control |  | 0: APP Control 11:SCM 12:Standby 13:Force Charge 14:Force Discharge |  |  | Write/Read | KEY control reg
|  | 57504 | 2 | export_limit |  | UINT32 | Grid-side export power limit (if not required, it can be set to a sufficiently large value so that it does not constrain system operation, e.g., 30 kW) | w | Write/Read
|  | 57506 | 2 | storage_set_point |  | UINT32 | Battery charge/discharge setpoint (active in Force Charge/Discharge modes). This value is always positive for both charging and discharging control |  | Write/Read
|  | 57508 | 1 | opModConnect/opModEnergize |  | UINT16 | bit0: 1:energize, 0:de-energize bit1: 1:connect 0:disconnect |  | Write/Read
|  | 57509 | 2 | op_mod_gen_lim_w |  | UINT32 | Charging (import) power limit on inverter side |  | Write/Read
|  | 57511 | 2 | op_mod_load_lim_w |  | UINT32 | Discharging (generation/export) power limit on inverter side (AC port limit) |  | Write/Read
|  | 57513 | 1 | ramp rate |  | UINT16 | Range: 0~10000 Scale factor: 100 Default value: 0 The configuration is persistent and will be retained after power cycle. Examples: Value 27 = 0.27%/s Value 100 = 1.00%/s Value 10000 = 100.00%/s Special case: Value 0 will be internally treated as 100%/s, effectively disabling the ramp rate limiting behavior. |  | Write/Read
90 | Battery | Pack Summary Information
91 |  | 51001 | 1 | Total Pack Parallel Quantity | uint | 1~16 | Quantity of parallel-connected Packs | / | Read
92 |  | 51002 | 1 | Total Pack Voltage | uint | 0~10000 | / | 0.1V | Read
93 |  | 51003 | 1 | Total Pack Current | uint | / | / | 0.1A | Read
94 |  | 51004 | 1 | Total Pack SOC | uint | 0~100 | Total state of charge | % | Read
95 |  | 51005 | 1 | Total Pack SOH | uint | 0~100 | Total state of health | % | Read
96 |  | 51006 | 1 | Total Pack Charging Status | enum | [0,1,2] | 0:Idle 1:Charging 2:Discharging | / | Read
97 |  | 51007 | 1 | Total Estimated Full Charge Time | uint | / | / | 1Min | Read
98 |  | 51008 | 1 | Total Estimated Full Discharge Time | uint | / | / | 1Min | Read
|  | 51009 | 2 | Maximum energy storage capacity of the DER | uint32 | / |  | WH | Read
|  | 51011 | 2 | Maximum energy storage capacity of the DER | uint32 | / |  | AH | Read
|  | 51013 | 1 | Rated battery voltage | uint16 | / |  | 0.1V | Read
|  | 51014 | 2 | Maximum rate of energy transfer received by the storage DER | uint32 | / |  | w | Read
|  | 51016 | 2 | Maximum rate of energy transfer delivered by the storage DER | uint32 | / |  | w | Read
99 |  | Each Pack Base Information
100 |  | 51200 | 6 | Pack Type | string | 1~12 | Pack type 12 ASCII characters-normal string order | / | Read
101 |  | 51206 | 4 | Pack SN Serial Number | uint | / | Serial Number | / | Read
102 |  | 51210 | 1 | Total Pack Software Number | uint | 1~10 | For the same version,only the lowest one is displayed | / | Read
103 |  | 51211 | 2 | Pack Software Version1 | uint | / | / | / | Read
104 |  | 51213 | 2 | Pack Software Version2 | uint | / | / | / | Read
105 |  | 51215 | 2 | Pack Software Version3 | uint | / | / | / | Read
106 |  | 51217 | 2 | Pack Software Version4 | uint | / | / | / | Read
107 |  | 51219 | 1 | Pack Voltage | uint | 0~10000 | / | 0.1V | Read
108 |  | 51220 | 1 | Pack Current | uint | 0~10000 | During charging,it refers to the charging current; During discharging,it refers to the discharging current. | 0.1A | Read
109 |  | 51221 | 1 | Pack SOC | uint | 0~100 | Single pack state of charge | % | Read
110 |  | 51222 | 1 | Pack SOH | uint | 0~100 | Single pack state of health | % | Read
111 |  | 51223 | 1 | Pack Cycle Count | uint | / | A complete charge-discharge process constitutes one cycle | / | Read
112 |  | 51224 | 1 | Pack Average Temperature | int | [-40~160] | / | 1℃ | Read
113 |  | 51234 | 1 | Pack Total Cell Count | uint | / | / | / | Read
114 |  | 51235 | 1 | Pack Total NTC Count | uint | 1~255 | / | / | Read
115 |  | 51236 | 2 | Pack Total Charging Energy | uint | / | Cumulative charging energy of the pack | 1Wh | Read
116 |  | 51238 | 2 | Pack Total Discharging Energy | uint | / | Cumulative discharging energy of the pack | 1Wh | Read
117 |  | 51240 | 2 | Pack Protect | uint | / | The BMS will disable input/output; bitwise representation | / | Read
118 |  | 51242 | 3 | Pack System Error | uint | / | The BMS will disable input/output; bitwise representation | / | Read
119 |  | 51245 | 1 | Pack Alarm (Residential ESS) | uint | / | Notify the upper system cease charging or discharging For detailed information, please refer to the Pack Alarm Table Sheet1 | / | Read
120 |  | 51246 | 2 | Pack Alarm (Portable ESS) | uint | / | For detailed information, please refer to the Pack Alarm Table Sheet2 | / | Read
121 |  | 51248 | 1 | Pack Estimated Full Charge Time | uint | / | / | 1Min | Read
122 |  | 51249 | 1 | Pack Estimated Full Discharge Time | uint | / | / | 1Min | Read
123 | IOT/HMI/common | IOT Basic Information/Monitoring Module Basic Information
124 |  | 53001 | 6 | IoT Model | string | / | Indicate the inverter main pack type | / | Read
125 |  | 53007 | 4 | IoT SN | uint | / | Serial number | / | Read
126 |  | 53011 | 2 | IoT Software Version | version | / | / | / | Read